## Sheet1
BACnet Points List Acuvim II
Object ID | Object Name | Object Description | Object Type
1 | Freq_rms | Frequency | Analog Input
2 | Ua_rms | Phase A Voltage | Analog Input
3 | Ub_rms | Phase B Voltage | Analog Input
4 | Uc_rms | Phase C Voltage | Analog Input
5 | Uavg_rms | Average Voltage | Analog Input
6 | Uab_rms | Line Voltage AB | Analog Input
7 | Ubc_rms | Line Voltage BC | Analog Input
8 | Uca_rms | Line Voltage CA | Analog Input
9 | Ulavg_rms | Average Line Voltage | Analog Input
10 | Ia_rms | Phase A Current | Analog Input
11 | Ib_rms | Phase B Current | Analog Input
12 | Ic_rms | Phase C Current | Analog Input
13 | Iavg_rms | Average Current | Analog Input
14 | In_rms | Neutral Current | Analog Input
15 | Pa_rms | Phase A Active Power | Analog Input
16 | Pb_rms | Phase B Active Power | Analog Input
17 | Pc_rms | Phase C Active Power | Analog Input
18 | P_rms | Total Active Power | Analog Input
19 | Qa_rms | Phase A Reactive Power | Analog Input
20 | Qb_rms | Phase B Reactive Power | Analog Input
21 | Qc_rms | Phase C Reactive Power | Analog Input
22 | Q_rms | Total Reactive Power | Analog Input
23 | Sa_rms | Phase A Apparent Power | Analog Input
24 | Sb_rms | Phase B Apparent Power | Analog Input
25 | Sc_rms | Phase C Apparent Power | Analog Input
26 | S_rms | Total Apparent Power | Analog Input
27 | PFa_rms | Phase A Power Factor | Analog Input
28 | PFb_rms | Phase B Power Factor | Analog Input
29 | PFc_rms | Phase C Power Factor | Analog Input
30 | PF_rms | Total Power Factor | Analog Input
31 | U_unbl | Voltage Unbalance Factor | Analog Input
32 | I_unbl | Current Unbalance Factor | Analog Input
33 | Rlc_val | Load Type | Analog Input
34 | P_dema | Active Power Demand | Analog Input
35 | Q_dema | Reactive Power Demand | Analog Input
36 | S_dema | Apparent Power Demand | Analog Input
37 | Ia_dema | Phase A Current Demand | Analog Input
38 | Ib_dema | Phase B Current Demand | Analog Input
39 | Ic_dema | Phase C Current Demand | Analog Input
40 | Active_Energy_Imp | Import Active Energy | Analog Input
41 | Active_Energy_Exp | Export Active Energy | Analog Input
42 | Reactive_Energy_Imp | Import Reactive Energy | Analog Input
43 | Reactive_Energy_Exp | Export Reactive Energy | Analog Input
44 | Active_Energy_Total | Total Energy | Analog Input
45 | Active_Energy_Net | Net Energy | Analog Input
46 | Reactive_Energy_Total | Total Reactive Energy | Analog Input
47 | Reactive_Energy_Net | Net Reactive Energy | Analog Input
48 | Apparent_Energy | Apparent Energy | Analog Input
49 | Active_Energy_Imp_A | Phase A Import Active Energy | Analog Input
50 | Active_Energy_Exp_A | Phase A Export Active Energy | Analog Input
51 | Active_Energy_Imp_B | Phase B Import Active Energy | Analog Input
52 | Active_Energy_Exp_B | Phase B Export Active Energy | Analog Input
53 | Active_Energy_Imp_C | Phase C Import Active Energy | Analog Input
54 | Active_Energy_Exp_C | Phase C Export Active Energy | Analog Input
55 | Reactive_Energy_Imp_A | Phase A Import Reactive Energy | Analog Input
56 | Reactive_Energy_Exp_A | Phase A Export Reactive Energy | Analog Input
57 | Reactive_Energy_Imp_B | Phase B Import Reactive Energy | Analog Input
58 | Reactive_Energy_Exp_B | Phase B Export Reactive Energy | Analog Input
59 | Reactive_Energy_Imp_C | Phase C Import Reactive Energy | Analog Input
60 | Reactive_Energy_Exp_C | Phase C Export Reactive Energy | Analog Input
61 | Apparent_Energy_A | Phase A Apparent Energy | Analog Input
62 | Apparent_Energy_B | Phase B Apparent Energy | Analog Input
63 | Apparent_Energy_C | Phase C Apparent Energy | Analog Input
64 | V1_thd | Phase A Voltage THD | Analog Input
65 | V2_thd | Phase B Voltage THD | Analog Input
66 | V3_thd | Phase C Voltage THD | Analog Input
67 | V_thd | Average Voltage THD | Analog Input
68 | I1_thd | Phase A Current THD | Analog Input
69 | I2_thd | Phase B Current THD | Analog Input
70 | I3_thd | Phase C Current THD | Analog Input
71 | I_thd | Average Current THD | Analog Input
72 | IO31_ai1 | IO31 Analog Input 1 | Analog Input
73 | IO31_ai2 | IO31 Analog Input 2 | Analog Input
74 | IO32_ai1 | IO32 Analog Input 1 | Analog Input
75 | IO32_ai2 | IO32 Analog Input 2 | Analog Input
76 | IO11_pc1 | IO11 Pulse Counter 1 | Analog Input
77 | IO11_pc2 | IO11 Pulse Counter 2 | Analog Input
78 | IO11_pc3 | IO11 Pulse Counter 3 | Analog Input
79 | IO11_pc4 | IO11 Pulse Counter 4 | Analog Input
80 | IO11_pc5 | IO11 Pulse Counter 5 | Analog Input
81 | IO11_pc6 | IO11 Pulse Counter 6 | Analog Input
82 | IO21_pc1 | IO21 Pulse Counter 1 | Analog Input
83 | IO21_pc2 | IO21 Pulse Counter 2 | Analog Input
84 | IO21_pc3 | IO21 Pulse Counter 3 | Analog Input
85 | IO21_pc4 | IO21 Pulse Counter 4 | Analog Input
86 | IO31_pc1 | IO31 Pulse Counter 1 | Analog Input
87 | IO31_pc2 | IO31 Pulse Counter 2 | Analog Input
88 | IO31_pc3 | IO31 Pulse Counter 3 | Analog Input
89 | IO31_pc4 | IO31 Pulse Counter 4 | Analog Input
90 | IO12_pc1 | IO12 Pulse Counter 1 | Analog Input
91 | IO12_pc2 | IO12 Pulse Counter 2 | Analog Input
92 | IO12_pc3 | IO12 Pulse Counter 3 | Analog Input
93 | IO12_pc4 | IO12 Pulse Counter 4 | Analog Input
94 | IO12_pc5 | IO12 Pulse Counter 5 | Analog Input
95 | IO12_pc6 | IO12 Pulse Counter 6 | Analog Input
96 | IO22_pc1 | IO22 Pulse Counter 1 | Analog Input
97 | IO22_pc2 | IO22 Pulse Counter 2 | Analog Input
98 | IO22_pc3 | IO22 Pulse Counter 3 | Analog Input
99 | IO22_pc4 | IO22 Pulse Counter 4 | Analog Input
100 | IO32_pc1 | IO32 Pulse Counter 1 | Analog Input
101 | IO32_pc2 | IO32 Pulse Counter 2 | Analog Input
102 | IO32_pc3 | IO32 Pulse Counter 3 | Analog Input
103 | IO32_pc4 | IO32 Pulse Counter 4 | Analog Input
1 | IO11_di1 | IO11 Digital Input 1 | Binary Input
2 | IO11_di2 | IO11 Digital Input 2 | Binary Input
3 | IO11_di3 | IO11 Digital Input 3 | Binary Input
4 | IO11_di4 | IO11 Digital Input 4 | Binary Input
5 | IO11_di5 | IO11 Digital Input 5 | Binary Input
6 | IO11_di6 | IO11 Digital Input 6 | Binary Input
7 | IO21_di1 | IO21 Digital Input 1 | Binary Input
8 | IO21_di2 | IO21 Digital Input 2 | Binary Input
9 | IO21_di3 | IO21 Digital Input 3 | Binary Input
10 | IO21_di4 | IO21 Digital Input 4 | Binary Input
11 | IO31_di1 | IO31 Digital Input 1 | Binary Input
12 | IO31_di2 | IO31 Digital Input 2 | Binary Input
13 | IO31_di3 | IO31 Digital Input 3 | Binary Input
14 | IO31_di4 | IO31 Digital Input 4 | Binary Input
15 | IO12_di1 | IO12 Digital Input 1 | Binary Input
16 | IO12_di2 | IO12 Digital Input 2 | Binary Input
17 | IO12_di3 | IO12 Digital Input 3 | Binary Input
18 | IO12_di4 | IO12 Digital Input 4 | Binary Input
19 | IO12_di5 | IO12 Digital Input 5 | Binary Input
20 | IO12_di6 | IO12 Digital Input 6 | Binary Input
21 | IO22_di1 | IO22 Digital Input 1 | Binary Input
22 | IO22_di2 | IO22 Digital Input 2 | Binary Input
23 | IO22_di3 | IO22 Digital Input 3 | Binary Input
24 | IO22_di4 | IO22 Digital Input 4 | Binary Input
25 | IO32_di1 | IO32 Digital Input 1 | Binary Input
26 | IO32_di2 | IO32 Digital Input 2 | Binary Input
27 | IO32_di3 | IO32 Digital Input 3 | Binary Input
28 | IO32_di4 | IO32 Digital Input 4 | Binary Input